## Summary
Report Name | Steam Trap Monitoring System report - Refinery FCCU
Report Start Date | 2026-07-06 23:59:00
Report End Date | 2026-07-07 23:59:00
Analysis Duration in Hrs | 24
Report Generated At | July 08, 2026 (Wed) at 08:31:15
Report Generated By | Sneh Lalka
Total Steam traps | 530
Status | Trap Count | % time of Duration
Normal | 448 | 86.54 % | Need Condition For defning in which satus is the Trap in
Leaking | 44 | 6.73 % |  |  | Pavan
Flooding | 0 | 0.0 % |  |  | 24/duration of the condtion
Choking | 0 | 0.0 %
Non Operational | 0 | 0.0 %
No Status | 0 | 0.0 %
Offline | 48 | 6.73 %
parameter | Count
Number of feedback | 0 |  |  | Condtion Of how we are Defning the Change in satus S1 Sensor | Corrective Action Data of how can i retive the data Sensor D11,D12 | Need Sensor And logic fo how we are defining this
Corrective Actions | 0 |  |  | Sushant
Status changes | 0
parameter | Numbers
Cost of Steam (Rs/Ton) | 2473.3333 |  |  | Need Sensor And Formula for calucating
Loss (MT) | 1.218 |  |  | Sushant
Savings (MT) | 6.962
Loss (INR) | 3012.52
Savings (INR) | 17219.3467

## Analysis
Sr No | Name | Device ID | Location | Department | Current Status | Duration | Normal | Flooding | Leaking | Choking | Non Operational | No Status | Offline | Change in Status | Number of Corrective Actions | Number of Feedbacks | Leak Rate | Cost of Steam | Saving | Loss
1 | 510-HPST-001 | STM_09025003 | 510E-102A-D EXPORT STEAM TO FGC TRAP PASSING NEAR HWB DOSING SKID | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
2 | 510-HPST-002 | STM_09025008 | Steam trap of HP Near Pump 510-P-303B | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 3483.24 | 0.00
3 | 510-HPST-003 | STM_09025001 | FGC OUTLETSTEAM LINE TO STEAM HEADER NEAR Col-N-34 | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
4 | 510-HPST-004 | STM_09025002 | HP steam main to 512-P-104 C main I/V d/s Steam trap | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
5 | 510-HPST-005 | STM_09025004 | HP STEAM TO MAB STEAM TRAP NEAR 510-P-202 B | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
6 | 510-HPST-006 | STM_09025006 | HP STEAM TO WGC STEAM TRAP NEAR 510-P-202 B | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
7 | 510-HPST-007 | STM_09025007 | HP STEAM TRAP OSBL VALVE d/s | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 3478.37 | 0.00
8 | 510-HPST-008 | STM_09025009 | STEAM TRAP OF HP STEAM MAIN HEADER NEAR 510-P-302B | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
9 | 510-HPST-009 | STM_09025013 | Steam Trap of HP steam to 510-E-301 A I/V u/s | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 150 Kg/hr | 2700 | 0.00 | 0.00
10 | 510-LPST-001 | STM_09025014 | LP STEAM TRAP IN BETWEEN OSBL AND ISBL VALVE | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 20 Kg/hr | 1800 | 0.00 | 0.00
11 | 510-LPST-002 | STM_09025011 | LP STEAM TRAP OSBL VALVE d/s | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 20 Kg/hr | 1800 | 0.00 | 0.00
12 | 510-MPST-001 | STM_09025005 | Steam trap of MP Near Pump 510-P -103B | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 50 Kg/hr | 2300 | 0.00 | 0.00
13 | 510-MPST-002 | STM_09025010 | MP STEAM TRAP IN BETWEEN OSBL AND ISBL VALVE | Mechanical | Heavy Leak | 24.00 hrs | 0.00 % | 0.00 % | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 50 Kg/hr | 2300 | 0.00 | 1218.28
14 | 510-MPST-003 | STM_09025015 | MP STEAM TRAP OSBL VALVE d/s | Mechanical | No Status | 24.00 hrs | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 100.00 % | 0 | 0 | 0 | 50 Kg/hr | 2300 | 0.00 | 0.00
15 | 510-MPST-004 | STM_09025012 | Steam Trap of MP steam main hdr near 510-P-303 B | Mechanical | Normal | 24.00 hrs | 100.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0.00 % | 0 | 0 | 0 | 50 Kg/hr | 2300 | 0.00 | 0.00

## Live Status
Sr No | Name | Device ID | Location | Department | Inlet Pressure (kg/cm²) | Outlet Pressure (kg/cm²) | Inlet BaseLine Temperature (°C) | Outlet BaseLine Temperature (°C) | Live Inlet Temperature (°C) | Live Outlet Temperature (°C) | Status | Description
1 | 510-HPST-001 | STM_09025003 | 510E-102A-D EXPORT STEAM TO FGC TRAP PASSING NEAR HWB DOSING SKID | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 216.67 | 87.18 | Normal | [2026-07-07 11:43 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
2 | 510-HPST-002 | STM_09025008 | Steam trap of HP Near Pump 510-P-303B | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 223.52 | 95.7 | Normal | [2026-07-07 11:50 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
3 | 510-HPST-003 | STM_09025001 | FGC OUTLETSTEAM LINE TO STEAM HEADER NEAR Col-N-34 | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 225.87 | 68.1 | Normal | [2026-07-07 11:34 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
4 | 510-HPST-004 | STM_09025002 | HP steam main to 512-P-104 C main I/V d/s Steam trap | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 259.52 | 96.47 | Normal | [2026-07-07 11:44 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
5 | 510-HPST-005 | STM_09025004 | HP STEAM TO MAB STEAM TRAP NEAR 510-P-202 B | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 224.19 | 85.06 | Normal | [2026-07-07 11:30 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
6 | 510-HPST-006 | STM_09025006 | HP STEAM TO WGC STEAM TRAP NEAR 510-P-202 B | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 231.66 | 97.31 | Normal | [2026-07-07 11:30 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
7 | 510-HPST-007 | STM_09025007 | HP STEAM TRAP OSBL VALVE d/s | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 221.74 | 96.47 | Normal | [2026-07-07 11:56 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
8 | 510-HPST-008 | STM_09025009 | STEAM TRAP OF HP STEAM MAIN HEADER NEAR 510-P-302B | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 227.22 | 100.52 | Normal | [2026-07-07 11:39 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
9 | 510-HPST-009 | STM_09025013 | Steam Trap of HP steam to 510-E-301 A I/V u/s | Mechanical | 35 kg/cm² | 1 kg/cm² | 243 °C | 100 °C | 226.75 | 96.38 | Normal | [2026-07-07 11:55 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 243.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
10 | 510-LPST-001 | STM_09025014 | LP STEAM TRAP IN BETWEEN OSBL AND ISBL VALVE | Mechanical | 3.5-4 kg/cm² | 1 kg/cm² | 147 °C | 100 °C | 140.06 | 82.77 | Normal | [2026-07-07 11:34 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 147.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
11 | 510-LPST-002 | STM_09025011 | LP STEAM TRAP OSBL VALVE d/s | Mechanical | 3.5-4 kg/cm² | 1 kg/cm² | 147 °C | 100 °C | 140.94 | 95.99 | Normal | [2026-07-07 11:36 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 147.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
12 | 510-MPST-001 | STM_09025005 | Steam trap of MP Near Pump 510-P -103B | Mechanical | 10-11 kg/cm² | 1 kg/cm² | 183 °C | 100 °C | 180.39 | 92.7 | Normal | [2026-07-07 11:46 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 183.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
13 | 510-MPST-002 | STM_09025010 | MP STEAM TRAP IN BETWEEN OSBL AND ISBL VALVE | Mechanical | 10-11 kg/cm² | 1 kg/cm² | 183 °C | 100 °C | 192.95 | 173 | Heavy Leak | [2026-07-07 11:32 PM] - Major leak means the trap is leaking the steam to the condensate discharge line. The trap is major leaking because outlet temperature is 75.1 degree Celsius above saturated 100.0 degree Celsius temperature. Meaning that steam is being leaking from the trap. Please note that if the trap is having a common condensate line, there can be a possibility of increased outlet temperature due to steam leak in adjacent traps. Here re-recommend to check and attend the trap that has maximum outlet temperature out of all the traps that are sharing the same condensate line. Also check the check valve, failure in check valve can also lead to increase in outlet pressure and leading in increase outlet temperature.
14 | 510-MPST-003 | STM_09025015 | MP STEAM TRAP OSBL VALVE d/s | Mechanical | 10-11 kg/cm² | 1 kg/cm² | 183 °C | 100 °C | 185.5 | - | No Status | The sensor is providing erroneous readings.
15 | 510-MPST-004 | STM_09025012 | Steam Trap of MP steam main hdr near 510-P-303 B | Mechanical | 10-11 kg/cm² | 1 kg/cm² | 183 °C | 100 °C | 181.82 | 96.31 | Normal | [2026-07-07 11:32 PM] - Normal means that trap is operating fine and is not having any issue. The status is normal as inlet is near saturated 183.0 degree Celsius temperature and outlet is below saturated 100.0 degree Celsius temperature
Need Description Sensor and how we can retive this
Sushant